## summary
field | value
export_id | pvu-export-20260404-204723
captured_at | 2026-04-04T17:47:23.842939+00:00
source_type | scenario
source_label | Межсезонье (midseason)
scenario_id | midseason
scenario_title | Межсезонье
status | normal
alarm_count | 0
trend_points | 13

## parameters
field | value
outdoor_temp_c | 6
airflow_m3_h | 3000
supply_temp_setpoint_c | 19
heat_recovery_efficiency | 0.45
heater_power_kw | 18
filter_contamination | 0.15
fan_speed_ratio | 0.86
room_temp_c | 21.2
room_heat_gain_kw | 4.2
room_volume_m3 | 250
room_thermal_capacity_kwh_per_k | 14
room_loss_coeff_kw_per_k | 0.18
control_mode | auto
horizon_minutes | 120
step_minutes | 10

## state
field | value
timestamp | 2026-04-04T17:47:23.842594Z
control_mode | auto
actual_airflow_m3_h | 2444.55
mixed_air_temp_c | 6
recovered_air_temp_c | 12.84
supply_temp_c | 19
room_temp_c | 21.2
heating_power_kw | 5.04
heater_load_ratio | 0.28
fan_power_kw | 1.04
total_power_kw | 6.08
energy_intensity_kw_per_1000_m3_h | 2.49
filter_pressure_drop_pa | 143.17
heat_balance_kw | -0.34
status | normal

## alarms
code | message | level
| Активных предупреждений нет. | info

## trend
minute | outdoor_temp_c | supply_temp_c | room_temp_c | heating_power_kw | total_power_kw | airflow_m3_h | filter_pressure_drop_pa
0 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
10 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
20 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
30 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
40 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
50 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
60 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
70 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
80 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
90 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
100 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
110 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17
120 | 6 | 19 | 21.2 | 5.04 | 6.08 | 2444.55 | 143.17